## 故障知识库
序号 | 海上陆上 | 创建人 | 创建人工号 | 故障名称 | 故障原因 | 处理方案 | 标签 | 故障代码 | 数据类型 | 机型 | 所需标签点 | 判断方式 | 创建时间 | 更新时间
1 | 海上 | 侯悦 | 138913 | 变桨轴X备用电源电压低 | 备用电源电压频繁掉落 | 带BPMM模块或EPD登机检查备用电源接线 | B | 21004_SC_PitchBatteryVoltageLowA1,21005_SC_PitchBatteryVoltageLowA2,21006_SC_PitchBatteryVoltageLowA3,21007_SC_PitchBatteryVoltageLowA1,21008_SC_PitchBatteryVoltageLowA2,21009_SC_PitchBatteryVoltageLowA3,2101007_SC_PitchBatteryVoltageLowA1,2101008_SC_PitchBatteryVoltageLowA2,2101009_SC_PitchBatteryVoltageLowA3,23007_SC_PitchBatteryVoltageLowA1,23008_SC_PitchBatteryVoltageLowA2,23009_SC_PitchBatteryVoltageLowA3 | SCADA | — | grPitch1DCLinkVoltage,grPitch2DCLinkVoltage,grPitch3DCLinkVoltage,grPitchBackupVoltage1,grPitchBackupVoltage2,grPitchBackupVoltage3 | 备用电源电压多次跌落，未达到20V | 2026-07-04 17:48:40 | 2026-08-11 10:27:39
2 | 海上 | 侯悦 | 138913 | 变桨轴X备用电源电压低 | 备用电源电压掉至20V或0V | 登机检查备用电源接线有无松动或保险丝有无松脱 | C | 21004_SC_PitchBatteryVoltageLowA1,21005_SC_PitchBatteryVoltageLowA2,21006_SC_PitchBatteryVoltageLowA3,21007_SC_PitchBatteryVoltageLowA1,21008_SC_PitchBatteryVoltageLowA2,21009_SC_PitchBatteryVoltageLowA3,2101007_SC_PitchBatteryVoltageLowA1,2101008_SC_PitchBatteryVoltageLowA2,2101009_SC_PitchBatteryVoltageLowA3,23007_SC_PitchBatteryVoltageLowA1,23008_SC_PitchBatteryVoltageLowA2,23009_SC_PitchBatteryVoltageLowA3 | SCADA | — | grPitch1DCLinkVoltage,grPitch2DCLinkVoltage,grPitch3DCLinkVoltage,grPitchBackupVoltage1,grPitchBackupVoltage2,grPitchBackupVoltage3 | 备用电源电压掉至20V或0V | 2026-07-04 17:48:40 | 2026-08-11 16:26:47
3 | 海上 | 侯悦 | 138913 | 变桨轴X备用电源电压低 | 主驱或从驱备用电源电压频繁掉落 | 登机检查备用电源接线，无异常则更换EPD | A | 21004_SC_PitchBatteryVoltageLowA1,21005_SC_PitchBatteryVoltageLowA2,21006_SC_PitchBatteryVoltageLowA3,21007_SC_PitchBatteryVoltageLowA1,21008_SC_PitchBatteryVoltageLowA2,21009_SC_PitchBatteryVoltageLowA3,2101007_SC_PitchBatteryVoltageLowA1,2101008_SC_PitchBatteryVoltageLowA2,2101009_SC_PitchBatteryVoltageLowA3,23007_SC_PitchBatteryVoltageLowA1,23008_SC_PitchBatteryVoltageLowA2,23009_SC_PitchBatteryVoltageLowA3 | SCADA | — | grPitch1DCLinkVoltage,grPitch2DCLinkVoltage,grPitch3DCLinkVoltage,grPitchBackupVoltage1,grPitchBackupVoltage2,grPitchBackupVoltage3 | 仅主/从驱后备电源电压跌落至440V以下 | 2026-03-30 16:55:23 | 2026-08-15 11:33:19