## fault_knowledge_sea
id | fault_name | all_fault_code | fault_reason | solution | label | data_type | tags | analytical_method | picture_path | sample_table_name | owner | owner_id | created_time | updated_time
1 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 机侧断路器柜跳闸 | 登机检查机侧断路器柜情况 | A | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 故障时刻前机舱断路器1或2或1和2的合闸反馈由1变成0 |  | 08014_sc_generatorspeedfromconvertererror | 刘宗沛 |  | 2026-03-12 16:51 | 2026-03-30 10:18
2 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 切变频器单机运行，启机时触发，机舱断路器柜正反接不对应 | 配置信息界面重新调整机舱断路器柜正反接 | B | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 运行模式12或13，发电机转速大于15，变频器发电机转速小于10 |  | 08014_sc_generatorspeedfromconvertererror | 刘宗沛 |  | 2026-03-12 16:51 | 2026-03-30 10:18
3 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 叶轮反转 | 停机，将机组手动对风后，重新启机即可 | C | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 发电机转速大于10，变频器发电机转速小于0，且发电机转速+变频器发电机转速小于10 |  | 08014_sc_generatorspeedfromconvertererror | 刘宗沛 |  | 2026-03-18 16:41 | 2026-03-30 10:18
4 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 启机状态或升速状态下，平均叶轮转速读取接近开关，且接近开关转速跳变或因接近开关转速迟滞性，导致发电机转速和变频器发电机转速偏差过大 | 处理好滑环编码器转速问题，使平均叶轮转速切换回读取滑环编码器 | D | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 运行模式11、12或13，发电机转速与变频器发电机转速偏差超过20，且接近开关转速存在跳变或明显迟滞现象 |  | 08014_sc_generatorspeedfromconvertererror | 刘宗沛 |  | 2026-03-19 08:47 | 2026-03-30 10:18
5 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 启机状态下，机舱断路器柜未合闸 | 检查变流器界面，变流器手动模式按钮是否没点灭，或变流器主从机未使能。若上述均正常，则手动测试机舱断路器柜分合闸，分合闸无误后，重新启机 | E | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 运行模式12、13，机舱断路器1和2的合闸反馈为0 |  | 08014_sc_generatorspeedfromconvertererror | 刘宗沛 |  | 2026-03-19 08:56 | 2026-03-30 10:18
6 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 变流器通讯闪断导致或引发的附带故障 | 处理变流器通讯闪断问题或其他变流器首触故障即可 | F | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 1、errorlist记录里，发电机转速故障（变流器）故障前，存在时间接近的变流器心跳类故障，且故障触发后快速自复位；因心跳类故障，变流器发电机转速快速掉0，且断路器合闸反馈变成0，发电机转速未能快速下降，此时心跳类故障自复位，运行模式切换成8以上，主控检测变流器发电机转速与发电机转速偏差过大，触发该故障。 或 2、故障前，变流器发电机转速存在频繁掉0情况，发电机转速或叶轮转速波动正常 |  | 08014_sc_generatorspeedfromconvertererror | 刘宗沛 |  | 2026-03-19 10:34 | 2026-03-30 10:18
7 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 变流器发电机转速偏差大 | 变频器重新切换一遍单机或双机运行，若问题依旧未解决，则登机检查发电机联轴器有无打滑 | G | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 发电机转速和变频器发电机转速都大于10且发电机转速-变频器发电机转速大于10 |  | 08014_sc_generatorspeedfromconvertererror | 刘宗沛 |  | 2026-03-20 22:46 | 2026-03-30 10:18