## fault_knowledge_sea
id | fault_name | all_fault_code | fault_reason | solution | label | data_type | tags | analytical_method | picture_path | sample_table_name
1 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 滑环编码器或接近开关无转速 | 按照《M0100017624-MySE海上风力发电机组转速故障排查处理方法》登机排查 | H | Tracelog |  | 滑环编码器或接近开关无转速，rotor_speed出现掉落的情况 |  | 14003_sc_rotorandgeneratorspeeddiffmax
2 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 接近开关转速跳变 | 1、按照《M0100017624-MySE海上风力发电机组转速故障排查处理方法》登机排查； 2；按照《M2D00015404-MySE6.25- MySE6.45- MySE8.3风力发电机组滑环组件分体整改方案》执行分体滑环技改。 | B | Tracelog |  | 超速继电器及计数模块检测接近开关转速跳变 |  | 14003_sc_rotorandgeneratorspeeddiffmax
3 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 发电机联轴器打滑 | 更换发电机联轴器 | C | Tracelog |  | 超速继电器及计数模块检测接近开关和滑环编码器转速平稳无跳变，发电机转速突然跌落，同时叶轮转速有升高趋势 |  | 14003_sc_rotorandgeneratorspeeddiffmax
4 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 发电机转速变化率超限 | 登机检查发电机联轴器是否打滑，检查防滑线 | D | Tracelog |  | 超速继电器及计数模块检测接近开关和滑环编码器转速平稳无跳变，发电机转速存在瞬时突变（一般是运行模式小于14的情况下） |  | 14003_sc_rotorandgeneratorspeeddiffmax
5 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 滑环编码器和接近开关转速均跳变 | 1、按照《M0100017624-MySE海上风力发电机组转速故障排查处理方法》登机排查； 2、按照《M2D00015404-MySE6.25- MySE6.45- MySE8.3风力发电机组滑环组件分体整改方案》执行分体滑环技改。 | E | Tracelog |  | 超速继电器及计数模块检测接近开关和滑环编码器转速均跳变 |  | 14003_sc_rotorandgeneratorspeeddiffmax
6 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 变流器检测发电机转速异常 | 导出变流器后台数据，查看变流器故障点并登机处理 | F | Tracelog |  | 超速继电器及计数模块检测接近开关和滑环编码器转速平稳无跳变，变流器检测发电机转速为0 或者突然掉落 |  | 14003_sc_rotorandgeneratorspeeddiffmax
7 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 风机背风反转 | 排查风速风向仪，重新对风 | G | Tracelog |  | 发电机转速与变流器检测发电机转速相同，但是变流器检测发电机转速为负值 |  | 14003_sc_rotorandgeneratorspeeddiffmax
8 | 叶轮和发电机转速偏差过大 | 14003_SC_RotorAndGeneratorSpeedDiffMax,14006_SC_RotorAndGeneratorSpeedDiffMax,1400003_SC_RotorAndGeneratorSpeedDiffMax,14013_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffOver15RPM,14007_SC_RotorAndGeneratorSpeedDiffMaxWarn,14011_SC_RotorAndGeneratorSpeedDiffMaxWarn | 滑环编码器转速跳变 | 1、按照《M0100017624-MySE海上风力发电机组转速故障排查处理方法》登机排查； 2、按照《M2D00015404-MySE6.25- MySE6.45- MySE8.3风力发电机组滑环组件分体整改方案》执行分体滑环技改。 | A | Tracelog |  | 超速继电器及计数模块检测滑环编码器转速跳变 |  | 14003_sc_rotorandgeneratorspeeddiffmax
1 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 机侧断路器柜跳闸 | 登机检查机侧断路器柜情况 | A | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 故障时刻前机舱断路器1或2或1和2的合闸反馈由1变成0 |  | 08014_sc_generatorspeedfromconvertererror
2 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 切变频器单机运行，启机时触发，机舱断路器柜正反接不对应 | 配置信息界面重新调整机舱断路器柜正反接 | B | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 运行模式12或13，发电机转速大于15，变频器发电机转速小于10 |  | 08014_sc_generatorspeedfromconvertererror
3 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 叶轮反转 | 停机，将机组手动对风后，重新启机即可 | C | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 发电机转速大于10，变频器发电机转速小于0，且发电机转速+变频器发电机转速小于10 |  | 08014_sc_generatorspeedfromconvertererror
4 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 启机状态或升速状态下，平均叶轮转速读取接近开关，且接近开关转速跳变或因接近开关转速迟滞性，导致发电机转速和变频器发电机转速偏差过大 | 处理好滑环编码器转速问题，使平均叶轮转速切换回读取滑环编码器 | D | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 运行模式11、12或13，发电机转速与变频器发电机转速偏差超过20，且接近开关转速存在跳变或明显迟滞现象 |  | 08014_sc_generatorspeedfromconvertererror
5 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 启机状态下，机舱断路器柜未合闸 | 检查变流器界面，变流器手动模式按钮是否没点灭，或变流器主从机未使能。若上述均正常，则手动测试机舱断路器柜分合闸，分合闸无误后，重新启机 | E | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 运行模式12、13，机舱断路器1和2的合闸反馈为0 |  | 08014_sc_generatorspeedfromconvertererror
6 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 变流器通讯闪断导致或引发的附带故障 | 处理变流器通讯闪断问题或其他变流器首触故障即可 | F | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 1、errorlist记录里，发电机转速故障（变流器）故障前，存在时间接近的变流器心跳类故障，且故障触发后快速自复位；因心跳类故障，变流器发电机转速快速掉0，且断路器合闸反馈变成0，发电机转速未能快速下降，此时心跳类故障自复位，运行模式切换成8以上，主控检测变流器发电机转速与发电机转速偏差过大，触发该故障。 或 2、故障前，变流器发电机转速存在频繁掉0情况，发电机转速或叶轮转速波动正常 |  | 08014_sc_generatorspeedfromconvertererror
7 | 发电机转速故障（变流器） | 08014_SC_GeneratorSpeedFromConverterError,08022_SC_GeneratorSpeedFromConverterError,1400011_SC_GeneratorSpeedFromConverterError,14005_SC_GeneratorSpeedFromConverterError | 变流器发电机转速偏差大 | 变频器重新切换一遍单机或双机运行，若问题依旧未解决，则登机检查发电机联轴器有无打滑 | G | Tracelog | ioperation_mode,generator_speed,converter_generator_speed,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule2,breaker_on_feedback1,breaker_on_feedback2 | 发电机转速和变频器发电机转速都大于10且发电机转速-变频器发电机转速大于10 |  | 08014_sc_generatorspeedfromconvertererror
0 | 变桨超速 | 2101045_SC_PitchOverSpeed,21035_SC_PitchOverSpeed,21043_SC_PitchOverSpeed,23071_SC_PitchOverSpeed | 接近开关转速跳变 | 1、检查接近开关线缆有无松动； 2、调节接近开关间隙，或检查接近开关是否损坏，若损坏，则更换接近开关； 3、检查机舱吊机有无碰撞滑环止转杆。 | A | Tracelog | grRotorSpeedFormSpeedRelay1,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule1,grRotorSpeedFromCounterModule2 | 1、叶轮转速计数模块2发生转速跳变 2、若无计数模块2标签点，则观察超速继电器转速2有无明显跳变 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨超速\典型图像\A_6e3be3d9.png | 2101045_sc_pitchoverspeed
1 | 变桨超速 | 2101045_SC_PitchOverSpeed,21035_SC_PitchOverSpeed,21043_SC_PitchOverSpeed,23071_SC_PitchOverSpeed | 转速信号传输回路接线异常/轮毂内超速继电器异常 | 1、测量轮毂内超速继电器模块供电电压是否正常； 2、检查轮毂内超速继电器是否损坏或者设置参数是否错误； 3、检查接近开关到变桨轴柜内信号传输回路接线有无异常。 | B | Tracelog | grRotorSpeedFormSpeedRelay1,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule1,grRotorSpeedFromCounterModule2 | 1、接近开关转速无明显异常波动 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨超速\典型图像\B_a4176583.png | 2101045_sc_pitchoverspeed
| 叶轮超速 | 1000007_SC_RotorSpeedMaxLevel1,1400004_SC_RotorSpeedMaxLevel1,1400005_SC_RotorSpeedMaxLevel2,1400015_SC_RotorSpeedMaxLeve3,14004_SC_RotorSpeedMaxLevel1,14005_SC_RotorSpeedMaxLevel2,14007_SC_RotorSpeedMaxLevel1,14008_SC_RotorSpeedMaxLevel2 | 叶轮转速取自计数模块1转速，计数模块1转速存在严重波动或跳变 | 暂屏蔽计数模块1转速后复位运行，后续登机检查编码器到计数模块1之间的接线，可重做线耳 | A | Tracelog |  | 滑环编码器两个数值，只有计数模块1转速存在严重波动，超速继电器转速波动相对平稳 |  | 1000007_sc_rotorspeedmaxlevel1
| 叶轮超速 | 1000007_SC_RotorSpeedMaxLevel1,1400004_SC_RotorSpeedMaxLevel1,1400005_SC_RotorSpeedMaxLevel2,1400015_SC_RotorSpeedMaxLeve3,14004_SC_RotorSpeedMaxLevel1,14005_SC_RotorSpeedMaxLevel2,14007_SC_RotorSpeedMaxLevel1,14008_SC_RotorSpeedMaxLevel2 | 滑环编码器转速规律波动或跳变导致 | 登机检查梅花联轴器固定，以及线路屏蔽情况 | B | Tracelog |  | 滑环编码器两个数值，计数模块1转速、超速继电器转速皆存在严重波动或跳变 |  | 1000007_sc_rotorspeedmaxlevel1
| 叶轮超速 | 1000007_SC_RotorSpeedMaxLevel1,1400004_SC_RotorSpeedMaxLevel1,1400005_SC_RotorSpeedMaxLevel2,1400015_SC_RotorSpeedMaxLeve3,14004_SC_RotorSpeedMaxLevel1,14005_SC_RotorSpeedMaxLevel2,14007_SC_RotorSpeedMaxLevel1,14008_SC_RotorSpeedMaxLevel2 | 主控叶轮转速读取接近开关，接近开关转速跳变 | 检查接近开关间隙，线路屏蔽情况 | C | Tracelog |  | 接近开关转速跳变 |  | 1000007_sc_rotorspeedmaxlevel1
| 叶轮超速 | 1000007_SC_RotorSpeedMaxLevel1,1400004_SC_RotorSpeedMaxLevel1,1400005_SC_RotorSpeedMaxLevel2,1400015_SC_RotorSpeedMaxLeve3,14004_SC_RotorSpeedMaxLevel1,14005_SC_RotorSpeedMaxLevel2,14007_SC_RotorSpeedMaxLevel1,14008_SC_RotorSpeedMaxLevel2 | 故障前瞬时风速突增，桨叶收桨不及时导致 | 待风速平稳后，复位运行 | D | Tracelog |  |  |  | 1000007_sc_rotorspeedmaxlevel1
| 叶轮超速 | 1000007_SC_RotorSpeedMaxLevel1,1400004_SC_RotorSpeedMaxLevel1,1400005_SC_RotorSpeedMaxLevel2,1400015_SC_RotorSpeedMaxLeve3,14004_SC_RotorSpeedMaxLevel1,14005_SC_RotorSpeedMaxLevel2,14007_SC_RotorSpeedMaxLevel1,14008_SC_RotorSpeedMaxLevel2 | 故障前风向变化大，故障时刻风向对风，发电机转速快速升高，桨叶收桨不及时，导致实际转速超限 | 待风向稳定后复位运行 | E | Tracelog |  |  |  | 1000007_sc_rotorspeedmaxlevel1
| 叶轮超速 | 1000007_SC_RotorSpeedMaxLevel1,1400004_SC_RotorSpeedMaxLevel1,1400005_SC_RotorSpeedMaxLevel2,1400015_SC_RotorSpeedMaxLeve3,14004_SC_RotorSpeedMaxLevel1,14005_SC_RotorSpeedMaxLevel2,14007_SC_RotorSpeedMaxLevel1,14008_SC_RotorSpeedMaxLevel2 | 在不存在以上原因存在的实际超速 |  | F | Tracelog |  | 6.45MW的叶轮转速最大值大于13.44rpm 8.0MW的叶轮转速最大值大于12.1rpm |  | 1000007_sc_rotorspeedmaxlevel1
| 叶轮超速 | 1000007_SC_RotorSpeedMaxLevel1,1400004_SC_RotorSpeedMaxLevel1,1400005_SC_RotorSpeedMaxLevel2,1400015_SC_RotorSpeedMaxLeve3,14004_SC_RotorSpeedMaxLevel1,14005_SC_RotorSpeedMaxLevel2,14007_SC_RotorSpeedMaxLevel1,14008_SC_RotorSpeedMaxLevel2 | 滑环编码器及接近开关转速皆存在波动或跳变 | 检查吊机有无干涉滑环，以及线路屏蔽情况 | G | Tracelog |  |  |  | 1000007_sc_rotorspeedmaxlevel1
| 安全链发电机超速 | 0100007_SC_SafetyGeneratorOverSpeed,01007_SC_SafetyGeneratorOverSpeed,01009_SC_SafetyGeneratorOverSpeed | 安全链回路线路异常或超速继电器异常 | 1、检查超速继电器或安全链回路接线以及对应的安全继电器 | A | Tracelog | grRotorSpeedFormSpeedRelay1,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule1,grRotorSpeedFromCounterModule2 | 1、故障时刻接近开关转速小于1.2倍的机型额度转速（5.5MW小于14.4） 2、接近开关转速波动正常，故障时刻实际未超速。 | \\Imzspc1065\故障分析系统数据\样本库\海上\安全链发电机超速\典型图像\A_d0b4bb98.png | 0100007_sc_safetygeneratoroverspeed
| 安全链发电机超速 | 0100007_SC_SafetyGeneratorOverSpeed,01007_SC_SafetyGeneratorOverSpeed,01009_SC_SafetyGeneratorOverSpeed | 实际转速超限，风速变化大，桨叶收桨不及时导致 | 1、待风速稳定后复位运行 2、及时更新最新版主控程序 | B | Tracelog | grRotorSpeedFormSpeedRelay1,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule1,grRotorSpeedFromCounterModule2 | 1、故障时刻接近开关转速大于1.2倍的机型额度转速（5.5MW大于14.4） 2、接近开关转速波动正常，故障时刻实际超速。 | \\Imzspc1065\故障分析系统数据\样本库\海上\安全链发电机超速\典型图像\B_81fcef1b.png,\\Imzspc1065\故障分析系统数据\样本库\海上\安全链发电机超速\典型图像\B_2c1c6041.png | 0100007_sc_safetygeneratoroverspeed
| 安全链发电机超速 | 0100007_SC_SafetyGeneratorOverSpeed,01007_SC_SafetyGeneratorOverSpeed,01009_SC_SafetyGeneratorOverSpeed | 接近开关转速跳变导致 | 1、带高迟滞接近开关登机检查接近开关有无损坏； 2、接近开关到码盘间隙是否正常； 3、检查接近开关到超速继电器2和计数模块2的接线有无松动； 4、检查机舱吊机有无碰撞滑环止转杆。 | C | Tracelog | grRotorSpeedFormSpeedRelay1,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule1,grRotorSpeedFromCounterModule2 | 1、发电机转速存在较大波动，平均叶轮转速波动平稳 2、叶轮转速超速继电器2转速或者计数模块2转速存在振幅大，波动较大 | \\Imzspc1065\故障分析系统数据\样本库\海上\安全链发电机超速\典型图像\C_3b917a63.png | 0100007_sc_safetygeneratoroverspeed
1 | 发电机超速 | 08015_SC_GeneratorSpeedMaxLevel1,08016_SC_GeneratorSpeedMaxLevel2,08023_SC_GeneratorSpeedMaxLevel1,1400012_SC_GeneratorSpeedMaxLevel1,14009_SC_GeneratorSpeedMaxLevel1,14010_SC_GeneraorSpeedMaxLevel2 | 并网状态下，风况原因导致实际超速 | 1、待风况稳定后可复位； 2、全场或单台机组频繁报出该故障，导出故障相关的StatusCode、ActionList、TraceLog发给技术或控制室申请控制程序优化。 | A | Tracelog |  | 1、风速短时间内增加较大，轮毂转速和发电机转速短时间内增加较大，期间存在桨叶快速收桨 |  | 08015_sc_generatorspeedmaxlevel1
2 | 发电机超速 | 08015_SC_GeneratorSpeedMaxLevel1,08016_SC_GeneratorSpeedMaxLevel2,08023_SC_GeneratorSpeedMaxLevel1,1400012_SC_GeneratorSpeedMaxLevel1,14009_SC_GeneratorSpeedMaxLevel1,14010_SC_GeneraorSpeedMaxLevel2 | 启动或升速状态下，轮毂转速跳变 | 1、登机检查接近开关，查线路和模块 | B | Tracelog |  | 1、非并网状态下，接近开关转速跳变，轮毂转速短时间内超过额定转速，引起发电机转速超过设定值 |  | 08015_sc_generatorspeedmaxlevel1
0 | 安全链叶轮超速 | 0100008_SC_SafetyRotorOverSpeed,01008_SC_SafetyRotorOverSpeed,01010_SC_SafetyRotorOverSpeed | 滑环编码器转速跳变 | 1、检查梅花联轴器有无松动或损坏 2、检查滑环编码器线束固定有无松动 3、检查机舱吊机有无碰撞滑环止转杆 | A | Tracelog | grRotorSpeedFormSpeedRelay1,grRotorSpeedFormSpeedRelay2,grRotorSpeedFromCounterModule1,grRotorSpeedFromCounterModule2,rotor_speed |  |  | 0100008_sc_safetyrotoroverspeed
1 | 安全链叶轮超速 | 0100008_SC_SafetyRotorOverSpeed,01008_SC_SafetyRotorOverSpeed,01010_SC_SafetyRotorOverSpeed | 滑环编码器转速规律波动 | 1、检查梅花联轴器有无松动或损坏 2、检查滑环编码器屏蔽线有无异常 3、检查CMS在线振动监测转速线有无干扰 | B | Tracelog
2 | 安全链叶轮超速 | 0100008_SC_SafetyRotorOverSpeed,01008_SC_SafetyRotorOverSpeed,01010_SC_SafetyRotorOverSpeed | 超速继电器转速异常 | 1、检查滑环编码器有无损坏 2、检查超速继电器1有无掉电或损坏 | C | Tracelog
3 | 安全链叶轮超速 | 0100008_SC_SafetyRotorOverSpeed,01008_SC_SafetyRotorOverSpeed,01010_SC_SafetyRotorOverSpeed | 转速未超限 | 1、检查超速对应的安全链回路接线有无松动 2、检查超速对应的安全链继电器和底座有无松动 | D | Tracelog
0 | 变桨心跳 | 21285_SC_PitchHeartbeatFault,23065_SC_PitchHeartbeatFault,21129_SC_PitchHeartbeatFault,2100001_SC_PitchHeartbeatFault | 变桨通讯闪断导致或卡滞 | 1、按照变桨心跳排查文档排查 | A | Tracelog | pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3,pitch_position_setpoint | 故障时刻前，三支桨叶角度变成0 |  | 21285_sc_pitchheartbeatfault
1 | 变桨心跳 | 21285_SC_PitchHeartbeatFault,23065_SC_PitchHeartbeatFault,21129_SC_PitchHeartbeatFault,2100001_SC_PitchHeartbeatFault | 变桨通讯无异常 | 1、导出变桨驱动器内部数据，查看内部故障记录，并对应处理 | B | Tracelog | pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3,pitch_position_setpoint | 故障时刻前，三支桨叶角度无变成0的情况 |  | 21285_sc_pitchheartbeatfault
2 | 变桨心跳 | 21285_SC_PitchHeartbeatFault,23065_SC_PitchHeartbeatFault,21129_SC_PitchHeartbeatFault,2100001_SC_PitchHeartbeatFault | 机舱到塔基通讯中断 | 1、检查塔基到机舱的交换机有无故障 2、检查机舱到塔基交换机光纤有无松动 3、检查机舱动力柜和信号柜有无断电，24V有无跳闸 4、检查机舱时间继电器有无故障 5、使用proneta扫描机组交换机网络拓扑，查找异常并处理 | C | Tracelog | pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3,pitch_position_setpoint | 1、机舱多个反馈信号数据丢失 2、errorlist记录里面出现较多机舱反馈点异常记录 |  | 21285_sc_pitchheartbeatfault
0 | 变桨轴X备用电源电压低 | 21004_SC_PitchBatteryVoltageLowA1,21005_SC_PitchBatteryVoltageLowA2,21006_SC_PitchBatteryVoltageLowA3,21007_SC_PitchBatteryVoltageLowA1,21008_SC_PitchBatteryVoltageLowA2,21009_SC_PitchBatteryVoltageLowA3,2101007_SC_PitchBatteryVoltageLowA1,2101008_SC_PitchBatteryVoltageLowA2,2101009_SC_PitchBatteryVoltageLowA3,23007_SC_PitchBatteryVoltageLowA1,23008_SC_PitchBatteryVoltageLowA2,23009_SC_PitchBatteryVoltageLowA3 | 软启芯片异常重启导致 | 1、升级软启自复位程序 | A | SCADA | grPitch1DCLinkVoltage,grPitch2DCLinkVoltage,grPitch3DCLinkVoltage,grPitchBackupVoltage1,grPitchBackupVoltage2,grPitchBackupVoltage3 | 1、主/从驱后备电源电压突然跌落至440V以下 2、同时，主/从驱直流母线电压与主/从驱后备电源电压一起跌落 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X备用电源电压低\典型图像\A_defb0287.png | 21004_sc_pitchbatteryvoltagelowa1
1 | 变桨轴X备用电源电压低 | 21004_SC_PitchBatteryVoltageLowA1,21005_SC_PitchBatteryVoltageLowA2,21006_SC_PitchBatteryVoltageLowA3,21007_SC_PitchBatteryVoltageLowA1,21008_SC_PitchBatteryVoltageLowA2,21009_SC_PitchBatteryVoltageLowA3,2101007_SC_PitchBatteryVoltageLowA1,2101008_SC_PitchBatteryVoltageLowA2,2101009_SC_PitchBatteryVoltageLowA3,23007_SC_PitchBatteryVoltageLowA1,23008_SC_PitchBatteryVoltageLowA2,23009_SC_PitchBatteryVoltageLowA3 | 充电二极管异常导致 | 1、更换驱动器 | B | SCADA | grPitch1DCLinkVoltage,grPitch2DCLinkVoltage,grPitch3DCLinkVoltage,grPitchBackupVoltage1,grPitchBackupVoltage2,grPitchBackupVoltage3 | 1、仅主/从驱后备电源电压跌落至440V以下 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X备用电源电压低\典型图像\B_c937aac4.png | 21004_sc_pitchbatteryvoltagelowa1
| 变桨轴X从驱后备电源电压欠压 | 21111_SC_gsInitPitchSlaveFaultBatteryVoltLowA1,21112_SC_gsInitPitchSlaveFaultBatteryVoltLowA2,21113_SC_gsInitPitchSlaveFaultBatteryVoltLowA3 | 软启芯片异常重启导致 | 1、升级软启自复位程序 | A | SCADA | grPitchSlaveBusVoltage1,grPitchSlaveBusVoltage2,grPitchSlaveBusVoltage3,grSlaveBackupVoltageA1,grSlaveBackupVoltageA2,grSlaveBackupVoltageA3 | 1、主/从驱后备电源电压突然跌落至440V以下 2、同时，主/从驱直流母线电压与主/从驱后备电源电压一起跌落 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X从驱后备电源电压欠压\典型图像\A_cca9c50e.png | 21111_sc_gsinitpitchslavefaultbatteryvoltlowa1
| 变桨轴X从驱后备电源电压欠压 | 21111_SC_gsInitPitchSlaveFaultBatteryVoltLowA1,21112_SC_gsInitPitchSlaveFaultBatteryVoltLowA2,21113_SC_gsInitPitchSlaveFaultBatteryVoltLowA3 | 充电二极管异常导致 | 1、更换驱动器 | B | SCADA | grPitchSlaveBusVoltage1,grPitchSlaveBusVoltage2,grPitchSlaveBusVoltage3,grSlaveBackupVoltageA1,grSlaveBackupVoltageA2,grSlaveBackupVoltageA3 | 1、仅主/从驱后备电源电压跌落至440V以下 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X从驱后备电源电压欠压\典型图像\B_36056773.png | 21111_sc_gsinitpitchslavefaultbatteryvoltlowa1
| 变桨编码器2AX故障 | 21036_SC_PitchEncoder2A1Fault,21037_SC_PitchEncoder2A2Fault,21038_SC_PitchEncoder2A3Fault,21055_SC_PitchEncoder2A3Fault,23039_SC_PitchEncoder2A1Fault,23040_SC_PitchEncoder2A2Fault,23041_SC_PitchEncoder2A3Fault,2101057_SC_PitchEncoder2A3Fault,2101056_SC_PitchEncoder2A2Fault,2101055_SC_PitchEncoder2A1Fault | 桨叶编码器跳变导致 | 1、检查桨叶编码器接线是否松动 2、检查桨叶编码器有无损坏，损坏则更换 | A | SCADA | OperationMode,grPitchAngle1A,grPitchAngle1B,grPitchAngle2A,grPitchAngle2B,grPitchAngle3A,grPitchAngle3B | 1、故障模式=6，且故障轴B编码器与A编码器不一致，存在跳变的情况 2、故障编号giFirstErrorNumber=2636/2637/2638（当首触故障为变桨编码器2A1/2A2/2A3故障时） | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨编码器2AX故障\典型图像\A_00705859.png | 21036_sc_pitchencoder2a1fault
| 变桨编码器2AX故障 | 21036_SC_PitchEncoder2A1Fault,21037_SC_PitchEncoder2A2Fault,21038_SC_PitchEncoder2A3Fault,21055_SC_PitchEncoder2A3Fault,23039_SC_PitchEncoder2A1Fault,23040_SC_PitchEncoder2A2Fault,23041_SC_PitchEncoder2A3Fault,2101057_SC_PitchEncoder2A3Fault,2101056_SC_PitchEncoder2A2Fault,2101055_SC_PitchEncoder2A1Fault | Busmaster卡程序问题 | 1、升级B卡程序 | B | SCADA | OperationMode,grPitchAngle1A,grPitchAngle1B,grPitchAngle2A,grPitchAngle2B,grPitchAngle3A,grPitchAngle3B | 1、故障模式=6，且故障轴B编码器与A编码器一致，不存在跳变情况 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨编码器2AX故障\典型图像\B_d43bee5b.png | 21036_sc_pitchencoder2a1fault
| 变桨轴X电机编码器故障 | 21020_SC_PitchEncoder1A1Fault,21021_SC_PitchEncoder1A2Fault,21022_SC_PitchEncoder1A3Fault,21026_SC_PitchEncoder1A1Fault,21027_SC_PitchEncoder1A2Fault,21028_SC_PitchEncoder1A3Fault,23023_SC_PitchEncoder1A1Fault,23024_SC_PitchEncoder1A2Fault,23025_SC_PitchEncoder1A3Fault,2101028_SC_PitchEncoder1A3Fault,2101027_SC_PitchEncoder1A2Fault,2101026_SC_PitchEncoder1A1Fault | 电机编码器到驱动器之间线缆异常/电机编码器本体损坏 | 1、检查故障轴电机编码器是否正常（绿灯是否亮） 2、检查故障轴电机编码器接线是否短路或者断路 3、检查电机编码器插头是否松动 4、更换电机编码器 | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3 | 1、故障轴变桨角度存在跳变情况，与其他正常轴变桨不同步 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X电机编码器故障\典型图像\A_551c5acf.png | 21020_sc_pitchencoder1a1fault
| 变桨通讯AX故障 | 21022_SC_PitchCommunicationMPCA1Fault,21023_SC_PitchCommunicationMPCA2Fault,21024_SC_PitchCommunicationMPCA3Fault,23019_SC_PitchCommunicationMPCA1Fault,23020_SC_PitchCommunicationMPCA2Fault,23021_SC_PitchCommunicationMPCA3Fault,21016_SC_PitchCommunicationMPCA1Fault,21017_SC_PitchCommunicationMPCA2Fault,21018_SC_PitchCommunicationMPCA3Fault,2101022_SC_PitchCommunicationMPCA1Fault,2101023_SC_PitchCommunicationMPCA2Fault,2101024_SC_PitchCommunicationMPCA3Fault,21092_SC_PitchAxis1MPCCommunicationFault,21108_SC_PitchAxis2MPCCommunicationFault,21124_SC_PitchAxis3MPCCommunicationFault,23087_SC_PitchAxis1MPCCommunicationFault,23103_SC_PitchAxis2MPCCommunicationFault,23119_SC_PitchAxis3MPCCommunicationFault | 变桨通讯线缆松动/损坏/电磁干扰 | 1、检查轴箱内通讯线屏蔽线接地是否正常 2、测量通讯线两端终端电阻是否是120Ω 3、检查滑环到变桨轴箱以及轴箱之间的通讯线接线是否松动 4、驱动器内部硬件或排线是否损坏 | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 | 1、故障轴变桨角度故障前后数值一致并维持一段时间 2、故障轴变桨角度、电流值保持不变（维持某个数值或者有微小变化，相邻周期变化值小于等于0.01°），时间区间至少维持0.1s（包含脱网时刻或者区间起点在脱网后2S内） | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨通讯AX故障\典型图像\A_f5efed8d.png | 21022_sc_pitchcommunicationmpca1fault
| 变桨轴X限位开关误触发 | 21131_SC_PitchBladesAt91Degree,21132_SC_PitchBlade1At91Degree,21133_SC_PitchBlade2At91Degree,21134_SC_PitchBlade3At91Degree,23067_SC_PitchBladesAt91Degree,23068_SC_PitchBlade1At91Degree,23069_SC_PitchBlade2At91Degree,23070_SC_PitchBlade3At91Degree,2100004_SC_PitchBladesAt91Degree,2100005_SC_PitchBlade1At91Degree,2100006_SC_PitchBlade2At91Degree,2100007_SC_PitchBlade3At91Degree,21287_SC_PitchBladesAt91Degree,21288_SC_PitchBlade1At91Degree,21290_SC_PitchBlade3At91Degree | 限位开关损坏/异物卡滞 | 1、查看限位开关是否被异物卡滞； 2、拨动限位开关，查看对应限位开关状态是否正常； 3、检查限位开关是否损坏 | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 | 1、故障轴变桨角度不跟随主控指令，且故障前保持不动； 2、故障轴电流为0 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X限位开关误触发\典型图像\A_0ef72cfc.png,\\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X限位开关误触发\典型图像\A_d15a2354.png | 21131_sc_pitchbladesat91degree
| 变桨AX限位开关与编码器不匹配 | 21044_SC_PitchMismatchLimitSwitchAndAEncoderA1,21046_SC_PitchMismatchLimitSwitchAndAEncoderA3,23036_SC_PitchMismatchLimitSwitchAndAEncoderA1,23037_SC_PitchMismatchLimitSwitchAndAEncoderA2,23038_SC_PitchMismatchLimitSwitchAndAEncoderA3 | 限位开关损坏/异物卡滞 | 1、查看限位开关是否被异物卡滞； 2、拨动限位开关，查看对应限位开关状态是否正常； 3、检查限位开关是否损坏 | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 | 1、故障轴变桨角度不跟随主控指令，且故障前保持不动； 2、故障轴电流为0 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨AX限位开关与编码器不匹配\典型图像\A_21b6ae52.png,\\Imzspc1065\故障分析系统数据\样本库\海上\变桨AX限位开关与编码器不匹配\典型图像\A_e060c008.png | 21044_sc_pitchmismatchlimitswitchandaencodera1
| 变桨轴X电机过温 | 21093_SC_PitchAxis1MotorOverTemperature,21109_SC_PitchAxis2MotorOverTemperature,21125_SC_PitchAxis3MotorOverTemperature,21129_SC_PitchAxis1MotorOverTemperature,21157_SC_PitchAxis2MotorOverTemperature,21185_SC_PitchAxis3MotorOverTemperature,23088_SC_PitchAxis1MotorOverTemperature,23104_SC_PitchAxis2MotorOverTemperature,23120_SC_PitchAxis3MotorOverTemperature,2101313_SC_PitchAxis1MotorOverTemperature,2101329_SC_PitchAxis2MotorOverTemperature,2101345_SC_PitchAxis3MotorOverTemperature | 变桨电机温度实际超温 | 1、手动变桨，查看电机工作状态，是否存在异响； 2、观察传动链有无卡涩情况，确认异常点； 3、更换变桨电机 | A | SCADA | OperationMode,grPitchMotorCurrent1,grPitchMotorCurrent2,grPitchMotorCurrent3,grPitchMotorTemperture1,grPitchMotorTemperture2,grPitchMotorTemperture3 | 1、故障轴电机温度≥130℃； 2、故障轴电机电流异常≥80A | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X电机过温\典型图像\A_01fa1126.png | 21093_sc_pitchaxis1motorovertemperature
| 变桨轴X电机过温 | 21093_SC_PitchAxis1MotorOverTemperature,21109_SC_PitchAxis2MotorOverTemperature,21125_SC_PitchAxis3MotorOverTemperature,21129_SC_PitchAxis1MotorOverTemperature,21157_SC_PitchAxis2MotorOverTemperature,21185_SC_PitchAxis3MotorOverTemperature,23088_SC_PitchAxis1MotorOverTemperature,23104_SC_PitchAxis2MotorOverTemperature,23120_SC_PitchAxis3MotorOverTemperature,2101313_SC_PitchAxis1MotorOverTemperature,2101329_SC_PitchAxis2MotorOverTemperature,2101345_SC_PitchAxis3MotorOverTemperature | 电机PT100/PT150温度传感器异常 | 1、检查PT100/PT150温度传感器接线是否松动，紧固接线； 2、检查PT100/PT150温度传感器是否损坏，若损坏更换备用PT100/PT150传感器 | B | SCADA | OperationMode,grPitchMotorCurrent1,grPitchMotorCurrent2,grPitchMotorCurrent3,grPitchMotorTemperture1,grPitchMotorTemperture2,grPitchMotorTemperture3 | 1、故障轴电机温度≥130℃； 2、故障轴电机电流无异常，没有出现大电流的情况（≥80A） | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X电机过温\典型图像\B_1bb0b848.png | 21093_sc_pitchaxis1motorovertemperature
1 | 变桨轴X驱动器输出错误 | 21081_SC_PitchAxis1MPCOutputFault,21097_SC_PitchAxis2MPCOutputFault,21113_SC_PitchAxis3MPCOutputFault,21173_SC_PitchAxis3MPCOutputFault,23076_SC_PitchAxis1MPCOutputFault,23092_SC_PitchAxis2MPCOutputFault,23108_SC_PitchAxis3MPCOutputFault,2101301_SC_PitchAxis1MPCOutputFault,2101317_SC_PitchAxis2MPCOutputFault,2101333_SC_PitchAxis3MPCOutputFault | E驱动器内部电机驱动单元损坏或电机电流检测回路失效 | 1、查看驱动器内部故障数据，查看OF故障报警频次； 2、若存在OF多次报警，且变桨电机及电机供电电缆无异常，直接更换EPD | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 | 1、故障前电流无异常，故障期间故障轴驱动器停止输出，电机电流为0； 2、故障期间故障轴变桨角度保持不变 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X驱动器输出错误\典型图像\A_56ab4c75.png | 21081_sc_pitchaxis1mpcoutputfault
2 | 变桨轴X驱动器输出错误 | 21081_SC_PitchAxis1MPCOutputFault,21097_SC_PitchAxis2MPCOutputFault,21113_SC_PitchAxis3MPCOutputFault,21173_SC_PitchAxis3MPCOutputFault,23076_SC_PitchAxis1MPCOutputFault,23092_SC_PitchAxis2MPCOutputFault,23108_SC_PitchAxis3MPCOutputFault,2101301_SC_PitchAxis1MPCOutputFault,2101317_SC_PitchAxis2MPCOutputFault,2101333_SC_PitchAxis3MPCOutputFault | 电机电源线短路或内部绕组短路 | 1、检查变桨电机电缆接线； 2、检查变桨电机三相绕组对地绝缘； 3、更换变桨电机 | B | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 | 1、故障轴变桨电机实际电流高于EPD的最高限制电流（EPD45＞120A；EPD55＞140A）； 2、故障期间故障轴变桨角度不跟随主控指令 | \\Imzspc1065\故障分析系统数据\样本库\海上\变桨轴X驱动器输出错误\典型图像\B_912333f9.png | 21081_sc_pitchaxis1mpcoutputfault
| 变桨跟随故障 | 23042_SC_PitchFollowingA1Fault,23043_SC_PitchFollowingA2Fault,23044_SC_PitchFollowingA3Fault,21291_SC_PitchFollowingA1Fault,21292_SC_PitchFollowingA2Fault,21293_SC_PitchFollowingA3Fault,21056_SC_PitchFollowingA1Fault,21057_SC_PitchFollowingA2Fault,21058_SC_PitchFollowingA3Fault,2100011_SC_PitchFollowingA1Fault,2100012_SC_PitchFollowingA2Fault,2100013_SC_PitchFollowingA3Fault | 变桨跟随异常 | 1、（故障机组报该故障频次少）检查滑环到变桨硬件EFC回路及变桨轴间通讯回路是否异常； 2、（故障机组报该故障频次高）检查驱动器故障记录，处理相应问题，以及检查滑环到变桨硬件EFC回路及变桨轴间通讯回路是否异常。 | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 |  |  | 23042_sc_pitchfollowinga1fault
| 变桨系统叶片间角度偏差大 | 21163_SC_PitchSystemSingleBladeDiff,21163_SC_PitchSystemSingleBladeDiff12,2100008_SC_PitchSystemSingleBladeDiff12,2100009_SC_PitchSystemSingleBladeDiff23,2100010_SC_PitchSystemSingleBladeDiff13,2100022_SC_PitchSystemSingleBladeDiff,21176_SC_PitchSystemSingleBladeDiff23,21177_SC_PitchSystemSingleBladeDiff13,21294_SC_PitchSystemSingleBladeDiff12,21295_SC_PitchSystemSingleBladeDiff23,21296_SC_PitchSystemSingleBladeDiff13,21297_SC_PitchSystemSingleBladeDiff | 变桨系统叶片间角度偏差大 | 需读取驱动器故障记录，处理相应问题 | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 |  |  | 21163_sc_pitchsystemsinglebladediff
| 变桨驱动器故障 | 21001_SC_PitchMPCA1Fault,21002_SC_PitchMPCA2Fault,21003_SC_PitchMPCA3Fault,2101001_SC_PitchMPCA1Fault,2101002_SC_PitchMPCA2Fault,2101003_SC_PitchMPCA3Fault,23001_SC_PitchMPCA1Fault,23002_SC_PitchMPCA2Fault,23003_SC_PitchMPCA3Fault | 驱动器故障 | 需根据机组报出具体变桨故障进行分析处理（或读取驱动器故障记录，处理相应问题） | A | Tracelog | ioperation_mode,pitch_position_setpoint,pitch_angle1,pitch_angle2,pitch_angle3,pitch_motor_current1,pitch_motor_current2,pitch_motor_current3 |  |  | 21001_sc_pitchmpca1fault